## Info
Capacity Test Calculator
Template version | 2.2
Generated at (UTC) | 2026-08-24 15:53:23
Site | Demo Site
Test run | Capacity test demo
Test run ID | 01KNSB4TTR8Y8G4WRX48GC1BB9
HelioTest status | failed
Reporting-condition method | percentile
Irradiance band (± %)
Regression fit window
Measured data inside the band
Modeled data inside the band
Bifaciality factor (φ) | 0.9
Structural shading factor (Sr) | 0.5
Regression terms enabled | irradiance, irradiance², temperature, wind
Pass/fail criterion | Test passing tolerance (±3%)
How this workbook calculates
All results on the Calculation sheet are computed live by Excel
formulas (LINEST) from the data sheets — recalculate at any time.
Regression form (ASTM E2848):
Capacity = E_RC * (a1 + a2*E_RC + a3*T_RC + a4*v_RC)
Pass/fail: configured capacity-ratio threshold tiers (per-band
one-sided minimums) supersede the symmetric test passing tolerance;
the Inputs sheet shows only the criterion this test run used.
The Cross-Check sheet compares Excel-computed values against the
values HelioTest computed when the test run was evaluated.
Reporting conditions and thresholds on the Inputs sheet (yellow
cells) are editable; all downstream results update on recalc.
Green/red highlighting marks PASS/FAIL verdicts and any
cross-check delta that is not zero.

## Inputs
Band | E_RC (W/m²) | T_RC (°C) | v_RC (m/s)
Low
Mid | 813 | 19.8 | 2.7
High
Pass/fail criteria — Tested Capacity Ratio (%)
Test passing tolerance (± %) | 3
Yellow cells are inputs — edit them and every result on the
Calculation sheet recalculates. Reporting conditions are needed
at least for the Mid band.

## Measured (Retained)
timestamp | power | t_amb | w_vel | e_total | e_sq | e_t | e_v | Filtered Measured Data Records (feeds the Tested Capacity regression)
2024-10-18 11:10:00 | 290.5182 | 22.6283 | 4.8317 | 795.1325 | 632235.6926 | 17992.5233 | 3841.8152
2024-10-18 11:15:00 | 295.0205 | 22.7883 | 5.2333 | 802.0517 | 643286.876 | 18277.4207 | 4197.4037 | Column | Meaning (ASTM E2848: P = E·(a1 + a2·E + a3·T + a4·v))
2024-10-18 11:20:00 | 297.7401 | 22.785 | 4.8317 | 812.2417 | 659736.5251 | 18506.9264 | 3924.481 | timestamp | Record timestamp
2024-10-18 11:25:00 | 300.0146 | 23.0267 | 5.705 | 820.595 | 673376.154 | 18895.5675 | 4681.4945 | power | Power output — the regression's dependent variable
2024-10-18 11:30:00 | 301.6923 | 22.905 | 4.7417 | 827.7058 | 685096.9465 | 18958.6021 | 3924.7052 | t_amb | Ambient air temperature T (°C)
2024-10-18 11:35:00 | 305.5337 | 23.225 | 4.4833 | 836.4033 | 699570.536 | 19425.4674 | 3749.8749 | w_vel | Wind speed v (m/s)
2024-10-18 11:40:00 | 306.3878 | 23.3683 | 4.3833 | 843.8425 | 712070.1648 | 19719.1928 | 3698.843 | e_total | Plane-of-array irradiance E (W/m²); for bifacial systems the total effective irradiance including the rear side
2024-10-18 11:45:00 | 309.0928 | 23.5367 | 4.1967 | 847.075 | 717536.0556 | 19937.3219 | 3554.8914 | e_sq | Regressor E² — e_total squared (live formula)
2024-10-18 11:50:00 | 307.5414 | 23.5117 | 4.05 | 852.2783 | 726378.3575 | 20038.4841 | 3451.7273 | e_t | Regressor E·T — e_total × t_amb (live formula)
2024-10-18 11:55:00 | 308.8681 | 23.7283 | 3.7467 | 854.7808 | 730650.273 | 20282.5245 | 3202.5789 | e_v | Regressor E·v — e_total × w_vel (live formula)
2024-10-18 12:00:00 | 309.467 | 23.5517 | 2.4033 | 857.6825 | 735619.2708 | 20199.8523 | 2061.2969
2024-10-18 12:05:00 | 306.991 | 22.63 | 2.8733 | 858.8117 | 737557.4788 | 19434.908 | 2467.6522
2024-10-18 12:10:00 | 311.6784 | 21.43 | 3.6183 | 864.4483 | 747270.921 | 18525.1278 | 3127.8622
2024-10-18 12:15:00 | 309.0095 | 21.6433 | 2.81 | 864.925 | 748095.2556 | 18719.8601 | 2430.4393
2024-10-18 12:20:00 | 309.7495 | 21.9217 | 3.6333 | 866.2575 | 750402.0563 | 18989.8082 | 3147.4022
2024-10-18 12:25:00 | 311.3473 | 21.2233 | 4.075 | 877.2342 | 769539.7832 | 18617.8331 | 3574.7292
2024-10-18 12:45:00 | 313.1696 | 21.195 | 4.3483 | 884.9425 | 783123.2283 | 18756.3563 | 3848.025
2024-10-18 12:50:00 | 315.6802 | 21.2483 | 4.1367 | 887.9833 | 788514.4003 | 18868.1659 | 3673.2911
2024-10-18 12:55:00 | 314.5168 | 21.2617 | 3.4467 | 885.8075 | 784654.9271 | 18833.7438 | 3053.0832
2024-10-18 13:00:00 | 315.2782 | 21.4017 | 4.7967 | 885 | 783225 | 18940.475 | 4245.05
2024-10-18 13:05:00 | 315.6425 | 21.1567 | 4.2483 | 881.8367 | 777635.9067 | 18656.7244 | 3746.3361
2024-10-18 13:10:00 | 312.8661 | 21.2717 | 4.1683 | 879.2383 | 773060.0468 | 18702.8647 | 3664.9585
2024-10-18 13:15:00 | 307.5655 | 21.445 | 3.6183 | 877.4933 | 769994.55 | 18817.8445 | 3175.0634
2024-10-18 13:20:00 | 310.123 | 21.5567 | 4.295 | 873.4583 | 762929.4601 | 18828.8501 | 3751.5035
2024-10-18 13:25:00 | 307.5681 | 22.05 | 3.1217 | 868.3408 | 754015.8028 | 19146.9154 | 2710.6706
2024-10-18 13:30:00 | 305.4272 | 22.0667 | 3.6467 | 862.8458 | 744502.9321 | 19040.1314 | 3146.5111
2024-10-18 13:35:00 | 303.2019 | 21.5983 | 4.1733 | 856.0775 | 732868.686 | 18489.8472 | 3572.6968
2024-10-18 13:40:00 | 300.2969 | 21.7217 | 3.1117 | 850.3108 | 723028.4155 | 18470.1672 | 2645.8837
2024-10-18 13:45:00 | 298.7046 | 21.6517 | 4.3569 | 843.7775 | 711960.4695 | 18269.1892 | 3676.2513
2024-10-18 13:50:00 | 294.2438 | 21.6672 | 4.3183 | 836.15 | 699146.8225 | 18117.0639 | 3610.7744
2024-10-18 13:55:00 | 294.5717 | 21.63 | 4.79 | 828.9425 | 687145.6683 | 17930.0263 | 3970.6346
2024-10-18 14:00:00 | 289.4469 | 21.61 | 4.7183 | 822.825 | 677040.9806 | 17781.2483 | 3882.3626
2024-10-18 14:05:00 | 288.1948 | 21.6 | 4.2583 | 815.3967 | 664871.724 | 17612.568 | 3472.2308
2024-10-18 14:10:00 | 284.42 | 21.49 | 5.42 | 807.5683 | 652166.613 | 17354.6435 | 4377.0204
2024-10-18 14:15:00 | 281.8153 | 21.41 | 4.4117 | 799.8425 | 639748.0248 | 17124.6279 | 3528.6385
2024-10-18 14:20:00 | 277.819 | 21.68 | 5.1317 | 789.5333 | 623362.8844 | 17117.0827 | 4051.6219
2024-10-18 14:25:00 | 273.7538 | 21.68 | 4.41 | 779.8233 | 608124.4312 | 16906.5699 | 3439.0209
2024-10-18 14:30:00 | 267.698 | 21.92 | 4.0483 | 767.3508 | 588827.3014 | 16820.3303 | 3106.492
2024-10-18 14:35:00 | 263.3931 | 22.15 | 2.8267 | 755.745 | 571150.505 | 16739.7517 | 2136.2392
2024-10-18 14:40:00 | 260.4062 | 22.28 | 2.83 | 744.1458 | 553753.0213 | 16579.5692 | 2105.9327
2024-10-18 14:45:00 | 255.8893 | 22.12 | 4.2467 | 733.6175 | 538194.6363 | 16227.6191 | 3115.429
2024-10-18 14:50:00 | 251.1278 | 22.03 | 4.17 | 721.1217 | 520016.4581 | 15886.3103 | 3007.0773
2024-10-18 14:55:00 | 244.6457 | 21.98 | 4.8017 | 709.0383 | 502735.3581 | 15584.6626 | 3404.5657
2024-10-18 15:00:00 | 239.7063 | 21.92 | 4.355 | 696.0733 | 484518.0854 | 15257.9275 | 3031.3994
2024-10-18 15:05:00 | 231.9615 | 22.22 | 3.635 | 682.5775 | 465912.0435 | 15166.872 | 2481.1692
2024-10-18 15:10:00 | 230.3495 | 21.9 | 5.0483 | 670.555 | 449644.008 | 14685.1545 | 3385.1852
2024-10-18 15:15:00 | 224.8371 | 21.58 | 4.9383 | 658.6333 | 433797.8678 | 14213.3073 | 3252.5509
2024-10-19 11:05:00 | 281.7348 | 26.48 | 6.39 | 775.6675 | 601660.0706 | 20539.6754 | 4956.5153
2024-10-19 11:10:00 | 283.7201 | 26.5567 | 6.0033 | 791.3833 | 626287.5803 | 21016.5034 | 4750.9379
2024-10-19 11:15:00 | 288.625 | 26.8767 | 5.6833 | 790.6325 | 625099.7501 | 21249.5662 | 4493.428
2024-10-19 11:20:00 | 290.6952 | 26.84 | 6.4967 | 791.7267 | 626831.1147 | 21249.9437 | 5143.5842
2024-10-19 11:25:00 | 300.3153 | 27.0567 | 4.9467 | 818.7933 | 670422.5227 | 22153.8183 | 4050.2977
2024-10-19 11:30:00 | 302.0552 | 27.12 | 4.7 | 825.755 | 681871.32 | 22394.4756 | 3881.0485
2024-10-19 11:35:00 | 303.7767 | 27.2967 | 5.0183 | 832.8775 | 693684.93 | 22734.7795 | 4179.6569
2024-10-19 11:40:00 | 299.8988 | 27.3567 | 4.7333 | 840.255 | 706028.465 | 22986.576 | 3977.207
2024-10-19 11:45:00 | 305.954 | 27.58 | 5.3333 | 845.5483 | 714951.984 | 23320.223 | 4509.5911
2024-10-19 11:50:00 | 310.3182 | 27.52 | 6.3833 | 852.0742 | 726030.3855 | 23449.0811 | 5439.0734
2024-10-19 11:55:00 | 311.8867 | 27.73 | 4.5383 | 855.6508 | 732138.3486 | 23727.1976 | 3883.2287
2024-10-19 12:00:00 | 306.1999 | 27.68 | 6.755 | 844.2158 | 712700.3733 | 23367.8943 | 5702.678
2024-10-19 12:05:00 | 309.3414 | 27.53 | 6.9817 | 853.935 | 729204.9842 | 23508.8305 | 5961.8895
2024-10-19 12:10:00 | 314.8421 | 27.66 | 5.965 | 869.8892 | 756707.1623 | 24061.1343 | 5188.8889
2024-10-19 12:15:00 | 313.301 | 27.92 | 5.125 | 871.9883 | 760363.6535 | 24345.9143 | 4468.9402
2024-10-19 12:20:00 | 315.1096 | 28.0233 | 5.3183 | 875.4442 | 766402.489 | 24532.8637 | 4655.9039
2024-10-19 12:25:00 | 314.0406 | 28.025 | 5.045 | 876.83 | 768830.8489 | 24573.1607 | 4423.6074
2024-10-19 12:30:00 | 315.5763 | 28.1033 | 5.1533 | 878.8733 | 772418.336 | 24699.2702 | 4529.1272
2024-10-19 12:35:00 | 314.5001 | 28.0967 | 4.755 | 879.92 | 774259.2064 | 24722.8189 | 4184.0196
2024-10-19 12:40:00 | 314.8505 | 28.1967 | 3.725 | 879.9208 | 774260.6729 | 24810.8344 | 3277.7051
2024-10-19 12:45:00 | 314.8448 | 28.48 | 4.08 | 880.385 | 775077.7482 | 25073.3648 | 3591.9708
2024-10-19 12:50:00 | 311.5162 | 27.0817 | 2.7633 | 872.1075 | 760571.4916 | 23618.1246 | 2409.9237
2024-10-19 12:55:00 | 310.0419 | 26.2833 | 2.0667 | 867.8033 | 753082.6253 | 22808.7643 | 1793.4602
2024-10-19 13:00:00 | 309.6951 | 26.71 | 2.0883 | 863.2467 | 745194.8075 | 23057.3185 | 1802.7468
2024-10-19 13:05:00 | 307.9727 | 26.9417 | 3.11 | 862.8842 | 744569.0851 | 23247.5376 | 2683.5698
2024-10-19 13:10:00 | 309.2284 | 27.405 | 3.7783 | 859.5775 | 738873.4785 | 23556.7214 | 3247.7703
2024-10-19 13:15:00 | 307.4595 | 25.9017 | 3.5383 | 855.0933 | 731184.6087 | 22148.3425 | 3025.6052
2024-10-19 13:20:00 | 308.2474 | 25.3667 | 3.3017 | 850.4617 | 723285.0465 | 21573.3776 | 2807.9409
2024-10-19 13:25:00 | 305.8577 | 25.2383 | 3.4883 | 845.0625 | 714130.6289 | 21327.9691 | 2947.8597
2024-10-19 13:30:00 | 301.2956 | 24.9317 | 2.9817 | 839.5117 | 704779.8385 | 20930.425 | 2503.144
2024-10-19 13:35:00 | 301.5702 | 24.84 | 2.9383 | 837.7267 | 701785.968 | 20809.1304 | 2461.5202
2024-10-19 13:40:00 | 298.9815 | 24.9067 | 2.8183 | 829.6983 | 688399.3243 | 20665.0198 | 2338.3665
2024-10-19 13:45:00 | 296.5824 | 24.0917 | 3.4567 | 825.5542 | 681539.6821 | 19888.9758 | 2853.6656
2024-10-19 13:50:00 | 295.5373 | 24.51 | 3.26 | 823.8475 | 678724.7033 | 20192.5022 | 2685.7429
2024-10-19 13:55:00 | 290.9552 | 24.5983 | 3.0967 | 813.7867 | 662248.7388 | 20017.7957 | 2520.026
2024-10-19 14:00:00 | 287.5451 | 24.4167 | 2.6967 | 806.0608 | 649734.067 | 19681.3187 | 2173.6774
2024-10-19 14:05:00 | 283.2494 | 24.6767 | 2.335 | 796.9087 | 635063.4545 | 19665.05 | 1860.7818
2024-10-19 14:10:00 | 281.2142 | 24.3867 | 2.8449 | 790.6439 | 625117.8409 | 19281.1702 | 2249.315
2024-10-19 14:15:00 | 277.1904 | 24.3417 | 2.53 | 781.4983 | 610739.645 | 19022.9719 | 1977.1908
2024-10-19 14:20:00 | 272.2719 | 23.79 | 2.7317 | 771.0892 | 594578.503 | 18344.2113 | 2106.3586
2024-10-19 14:25:00 | 269.4042 | 23.65 | 2.79 | 762.2742 | 581061.9052 | 18027.784 | 2126.7449
2024-10-19 14:30:00 | 265.2809 | 24.18 | 2.5333 | 752.4598 | 566195.7056 | 18194.4772 | 1906.2314
2024-10-19 14:35:00 | 259.6549 | 24.38 | 1.9317 | 741.6742 | 550080.5695 | 18082.0162 | 1432.6673
2024-10-19 14:40:00 | 255.8685 | 24.08 | 2.2117 | 730.5775 | 533743.4835 | 17592.3062 | 1615.7939
2024-10-19 14:45:00 | 251.0026 | 23.77 | 2.4767 | 720.1233 | 518577.6152 | 17117.3316 | 1783.5055
2024-10-19 14:50:00 | 246.3006 | 23.98 | 2.1 | 709.8792 | 503928.4313 | 17022.9024 | 1490.7462
2024-10-19 14:55:00 | 239.8134 | 24.75 | 1.9383 | 696.5817 | 485226.0183 | 17240.3963 | 1350.2075
2024-10-19 15:00:00 | 234.7999 | 24.27 | 1.8667 | 685.1383 | 469414.5358 | 16628.3073 | 1278.9249
2024-10-19 15:05:00 | 230.3984 | 24.34 | 2.1367 | 670.9883 | 450225.3435 | 16331.856 | 1433.6784
2024-10-19 15:10:00 | 224.6855 | 24.38 | 1.2317 | 656.3867 | 430843.4562 | 16002.7069 | 808.4496
2024-10-20 11:00:00 | 268.0066 | 24.51 | 1.365 | 738.4242 | 545270.2499 | 18098.7763 | 1007.949
2024-10-20 11:05:00 | 271.4708 | 24.46 | 0.99667 | 747.1942 | 558299.1227 | 18276.3693 | 744.7035
2024-10-20 11:10:00 | 272.5157 | 24.92 | 0.64167 | 757.2692 | 573456.5908 | 18871.1476 | 485.9144
2024-10-20 11:15:00 | 276.5122 | 24.83 | 0.84167 | 765.5083 | 586003.0084 | 19007.5719 | 644.3028
2024-10-20 11:20:00 | 280.5052 | 24.89 | 0.86667 | 774.9683 | 600575.9177 | 19288.9618 | 671.6392
2024-10-20 11:25:00 | 282.8572 | 25.38 | 1.5817 | 784.5892 | 615580.1605 | 19912.8731 | 1240.9585
2024-10-20 11:30:00 | 286.0464 | 25.3 | 1.855 | 792.9375 | 628749.8789 | 20061.3188 | 1470.8991
2024-10-20 11:35:00 | 288.6313 | 25.24 | 2.205 | 802.3025 | 643689.3015 | 20250.1151 | 1769.077
2024-10-20 11:40:00 | 291.8352 | 25.63 | 1.9233 | 809.9558 | 656028.452 | 20759.168 | 1557.8151
2024-10-20 11:45:00 | 293.3955 | 25.46 | 2.1667 | 817.2067 | 667826.736 | 20806.0817 | 1770.6144
2024-10-20 11:50:00 | 297.4685 | 25.33 | 2.525 | 823.8175 | 678675.2733 | 20867.2973 | 2080.1392
2024-10-20 11:55:00 | 300.4493 | 25.34 | 2.3033 | 829.6633 | 688341.2467 | 21023.6689 | 1910.9912
2024-10-20 12:00:00 | 301.2369 | 24.96 | 2.46 | 835.2633 | 697664.836 | 20848.1728 | 2054.7478
2024-10-20 12:05:00 | 303.3704 | 24.78 | 2.5533 | 840.2633 | 706042.4693 | 20821.7254 | 2145.4724
2024-10-20 12:10:00 | 305.16 | 24.6 | 2.5217 | 845.2617 | 714467.2851 | 20793.437 | 2131.4682
2024-10-20 12:15:00 | 305.7493 | 24.7 | 2.1433 | 849.797 | 722154.9119 | 20989.9855 | 1821.3982
2024-10-20 12:20:00 | 307.1456 | 24.35 | 2.4433 | 853.7275 | 728850.6443 | 20788.2646 | 2085.9409
2024-10-20 12:25:00 | 307.9006 | 24.1772 | 2.4373 | 855.6942 | 732212.5069 | 20688.283 | 2085.5732
2024-10-20 12:30:00 | 306.5534 | 23.7717 | 2.25 | 858.21 | 736524.4041 | 20401.082 | 1930.9725
2024-10-20 12:35:00 | 307.7688 | 23.8933 | 2.3417 | 860.9008 | 741150.2448 | 20569.7906 | 2015.9428
2024-10-20 12:40:00 | 306.2379 | 24.3717 | 1.77 | 861.8167 | 742727.9669 | 21003.9085 | 1525.4155
2024-10-20 12:45:00 | 307.9689 | 24.2967 | 2.65 | 863.4489 | 745543.9512 | 20978.9294 | 2288.1395
2024-10-20 12:50:00 | 308.6955 | 24.1967 | 2.38 | 862.5208 | 743942.1879 | 20870.1291 | 2052.7996
2024-10-20 12:55:00 | 307.7494 | 24.2833 | 2.2167 | 859.6867 | 739061.1648 | 20876.0579 | 1905.6388
2024-10-20 13:00:00 | 305.802 | 24.4033 | 2.0483 | 855.9942 | 732726.0134 | 20889.111 | 1753.3614
2024-10-20 13:05:00 | 305.5417 | 24.3917 | 1.685 | 855.9108 | 732583.3546 | 20877.0917 | 1442.2098
2024-10-20 13:10:00 | 304.2277 | 24.445 | 2.4117 | 853.0792 | 727744.0646 | 20853.5202 | 2057.3426
2024-10-20 13:15:00 | 303.7831 | 24.24 | 2.6267 | 849.2342 | 721198.6698 | 20585.4362 | 2230.6551
2024-10-20 13:20:00 | 301.1168 | 24.12 | 2.1317 | 843.2283 | 711034.0221 | 20338.6674 | 1797.4817
2024-10-20 13:25:00 | 299.1923 | 24.345 | 2.13 | 839.4175 | 704621.7393 | 20435.619 | 1787.9593
2024-10-20 13:30:00 | 296.4379 | 23.8683 | 1.9433 | 835.7158 | 698420.9541 | 19947.1441 | 1624.0744
2024-10-20 13:35:00 | 294.168 | 23.84 | 1.7333 | 829.85 | 688651.0225 | 19783.624 | 1438.4067
2024-10-20 13:40:00 | 292.8453 | 24.075 | 2.1083 | 824.9775 | 680587.8755 | 19861.3333 | 1739.3276
2024-10-20 13:45:00 | 289.4627 | 23.765 | 2.0317 | 817.8708 | 668912.7 | 19436.7004 | 1661.6409
2024-10-20 13:50:00 | 286.5275 | 24.1467 | 2.3233 | 811.9292 | 659228.9717 | 19605.3829 | 1886.3821
2024-10-20 13:55:00 | 285.0074 | 23.8167 | 2.6083 | 806.97 | 651200.5809 | 19219.3355 | 2104.8467
2024-10-20 14:00:00 | 282.5255 | 23.98 | 2.1517 | 798.08 | 636931.6864 | 19137.9584 | 1717.2021
2024-10-20 14:05:00 | 279.6966 | 24 | 2.4567 | 791.1067 | 625849.758 | 18986.56 | 1943.4854
2024-10-20 14:10:00 | 275.1339 | 23.8133 | 2.5717 | 783.0033 | 613094.22 | 18645.9194 | 2013.6236
2024-10-20 14:15:00 | 271.5382 | 23.8267 | 2.15 | 774.8333 | 600366.6944 | 18461.6956 | 1665.8917
2024-10-20 14:20:00 | 267.8953 | 23.8333 | 2.0217 | 763.3533 | 582708.3115 | 18193.2544 | 1543.246
2024-10-20 14:25:00 | 264.1551 | 23.8867 | 2.1367 | 752.8108 | 566724.1508 | 17982.1414 | 1608.5058
2024-10-20 14:30:00 | 258.5594 | 24.2033 | 1.665 | 743.0525 | 552127.0178 | 17984.3473 | 1237.1824
2024-10-20 14:35:00 | 255.7807 | 24.0567 | 1.8483 | 732.3642 | 536357.2726 | 17618.2406 | 1353.6531
2024-10-20 14:40:00 | 249.9974 | 24.355 | 1.7833 | 721.7758 | 520960.3536 | 17578.8504 | 1287.1669
2024-10-20 14:45:00 | 242.6598 | 24.3717 | 1.89 | 710.2983 | 504523.7223 | 17311.1542 | 1342.4638
2024-10-20 14:50:00 | 241.1886 | 24.3117 | 1.8383 | 699.4233 | 489192.9992 | 17004.1469 | 1285.7732
2024-10-20 14:55:00 | 235.6429 | 24.595 | 1.6483 | 686.9558 | 471908.317 | 16895.6787 | 1132.3322
2024-10-20 15:00:00 | 229.8613 | 24.48 | 1.5783 | 673.85 | 454073.8225 | 16495.848 | 1063.5599
2024-10-20 15:05:00 | 226.2269 | 24.565 | 1.79 | 660.8683 | 436746.954 | 16234.2306 | 1182.9543
2024-10-21 11:00:00 | 263.1438 | 21.81 | 2.1883 | 725.7958 | 526779.5917 | 15829.6071 | 1588.2832
2024-10-21 11:05:00 | 271.8151 | 20.92 | 2.9567 | 749.235 | 561353.0852 | 15673.9962 | 2215.2382
2024-10-21 11:20:00 | 273.2798 | 20.0356 | 2.915 | 759.9033 | 577453.076 | 15225.1141 | 2215.1182
2024-10-21 11:25:00 | 267.1203 | 20.1117 | 2.7133 | 740.8917 | 548920.4617 | 14900.5662 | 2010.2861
2024-10-21 11:30:00 | 277.2143 | 20.4407 | 2.6466 | 776.7075 | 603274.5406 | 15876.4279 | 2055.5966
2024-10-21 11:35:00 | 293.2096 | 20.44 | 2.5033 | 819.855 | 672162.221 | 16757.8362 | 2052.3703
2024-10-21 11:40:00 | 282.4502 | 20.325 | 2.6 | 786.9992 | 619367.6883 | 15995.7581 | 2046.1978
2024-10-21 11:45:00 | 295.0997 | 20.23 | 2.14 | 821.7215 | 675226.1725 | 16623.4253 | 1758.4839
2024-10-21 11:50:00 | 285.0198 | 20.6767 | 2.7633 | 801.145 | 641833.311 | 16565.0081 | 2213.8307
2024-10-21 11:55:00 | 287.3596 | 20.34 | 2.5733 | 803.3775 | 645415.4075 | 16340.6984 | 2067.3581
2024-10-21 12:00:00 | 266.792 | 20.4767 | 2.8367 | 742.7725 | 551710.9868 | 15209.5049 | 2106.998
2024-10-21 12:05:00 | 271.827 | 20.5383 | 2.77 | 762.5792 | 581526.9854 | 15662.1051 | 2112.3443
2024-10-21 12:10:00 | 267.6411 | 20.7083 | 3.0417 | 757.3867 | 573634.5628 | 15684.2156 | 2303.7178
2024-10-21 12:15:00 | 282.7824 | 20.7033 | 2.3817 | 791.645 | 626701.806 | 16389.6903 | 1885.4345
2024-10-21 12:20:00 | 291.0165 | 21.1533 | 1.6517 | 826.1517 | 682526.5763 | 17475.8616 | 1364.5272
2024-10-21 12:25:00 | 302.9966 | 21.075 | 3.4467 | 853.125 | 727822.2656 | 17979.6094 | 2940.4375
2024-10-21 12:35:00 | 284.559 | 21.2183 | 3.55 | 815.7142 | 665389.6017 | 17308.0951 | 2895.7853
2024-10-21 12:40:00 | 303.7311 | 20.7883 | 2.7583 | 863.6133 | 745827.9895 | 17953.0818 | 2382.1334
2024-10-21 12:45:00 | 305.7277 | 21.26 | 2.18 | 867.2433 | 752110.9992 | 18437.5933 | 1890.5905
2024-10-21 12:50:00 | 313.9147 | 21.8333 | 2.2533 | 889.6125 | 791410.4002 | 19423.2062 | 2004.5935
2024-10-21 12:55:00 | 296.408 | 21.5317 | 2.5667 | 846.9325 | 717294.6596 | 18235.8683 | 2173.7934
2024-10-21 13:00:00 | 245.383 | 21.9983 | 2.01 | 703.1033 | 494354.2973 | 15467.1015 | 1413.2377
2024-10-21 13:05:00 | 269.3627 | 21.8733 | 2.9717 | 747.0417 | 558071.2517 | 16340.2914 | 2219.9588
2024-10-21 13:10:00 | 298.1836 | 21.7717 | 2.4817 | 842.3992 | 709636.356 | 18340.4339 | 2090.5539
2024-10-21 13:15:00 | 287.5706 | 21.5467 | 3.1233 | 809.365 | 655071.7032 | 17439.1179 | 2527.9167
2024-10-21 13:20:00 | 301.7401 | 21.1267 | 2.475 | 857.6942 | 735639.2835 | 18120.2188 | 2122.7931
2024-10-21 13:25:00 | 280.847 | 21.0183 | 2.6667 | 790.8683 | 625472.7207 | 16622.7343 | 2108.9822
2024-10-21 13:30:00 | 288.8104 | 21.0667 | 2.0483 | 821.3633 | 674637.7253 | 17303.3876 | 1682.4259
2024-10-21 13:35:00 | 299.6022 | 21.0483 | 2.5067 | 849.9967 | 722494.3333 | 17891.0132 | 2130.6583
2024-10-21 13:40:00 | 296.1424 | 21.195 | 2.6733 | 844.1492 | 712587.8156 | 17891.7416 | 2256.6921
2024-10-21 13:45:00 | 293.7175 | 21.3867 | 2.285 | 831.6233 | 691597.3685 | 17785.651 | 1900.2593
2024-10-21 13:50:00 | 289.2945 | 21.6833 | 2.21 | 824.78 | 680262.0484 | 17883.9797 | 1822.7638
2024-10-21 13:55:00 | 285.5546 | 21.5567 | 2.375 | 815.6242 | 665242.7813 | 17582.1383 | 1937.1074
2024-10-21 14:00:00 | 281.9419 | 21.4917 | 3.1033 | 805.5742 | 648949.738 | 17313.1315 | 2499.9652
2024-10-21 14:05:00 | 278.124 | 21.6817 | 2.725 | 797.5092 | 636020.8709 | 17291.3279 | 2173.2125
2024-10-21 14:10:00 | 272.7092 | 21.4317 | 2.4533 | 787.0583 | 619460.8201 | 16867.9718 | 1930.9164
2024-10-21 14:15:00 | 271.5761 | 21.2967 | 2.15 | 777.0842 | 603859.8021 | 16549.3025 | 1670.731
2024-10-21 14:20:00 | 266.2998 | 21.165 | 2.61 | 766.6283 | 587719.0015 | 16225.6887 | 2000.9
2024-10-21 14:25:00 | 263.0942 | 20.7617 | 2.9683 | 757.4292 | 573698.9425 | 15725.4919 | 2248.3022
2024-10-21 14:30:00 | 260.1366 | 20.4317 | 2.535 | 746.8792 | 557828.4896 | 15259.9862 | 1893.3387
2024-10-21 14:35:00 | 254.3351 | 20.63 | 2.16 | 736.725 | 542763.7256 | 15198.6367 | 1591.326
2024-10-21 14:40:00 | 249.7449 | 20.825 | 2.2617 | 724.835 | 525385.7772 | 15094.6889 | 1639.3352
2024-10-21 14:45:00 | 244.7622 | 20.5683 | 2.405 | 713.9075 | 509663.9186 | 14683.8874 | 1716.9475
2024-10-21 14:50:00 | 240.1063 | 20.9917 | 2.0383 | 701.5967 | 492237.8827 | 14727.6834 | 1430.0879
2024-10-21 14:55:00 | 235.2303 | 20.655 | 2.05 | 689.6075 | 475558.5041 | 14243.8429 | 1413.6954
2024-10-21 15:00:00 | 230.2219 | 20.8783 | 2.3317 | 677.695 | 459270.513 | 14149.1421 | 1580.1588
2024-10-21 15:05:00 | 225.5113 | 20.655 | 1.8767 | 663.3792 | 440071.9188 | 13702.0967 | 1244.9416
2024-10-22 11:00:00 | 269.2593 | 21.1667 | 2.4617 | 746.0817 | 556637.8533 | 15792.0619 | 1836.6044
2024-10-22 11:05:00 | 273.8912 | 21.16 | 2.195 | 756.6358 | 572497.7843 | 16010.4142 | 1660.8157
2024-10-22 11:10:00 | 275.308 | 21.14 | 2.335 | 766.3617 | 587310.2041 | 16200.8856 | 1789.4545
2024-10-22 11:15:00 | 279.1561 | 21.0133 | 2.295 | 775.6542 | 601639.3863 | 16299.0796 | 1780.1263
2024-10-22 11:20:00 | 282.2374 | 21.2067 | 1.3567 | 783.6567 | 614117.7712 | 16618.7457 | 1063.1609
2024-10-22 11:25:00 | 284.1535 | 21.6067 | 1.47 | 792.1125 | 627442.2127 | 17114.9108 | 1164.4054
2024-10-22 11:30:00 | 288.1254 | 21.6933 | 1.78 | 799.3517 | 638963.087 | 17340.6022 | 1422.846
2024-10-22 11:35:00 | 290.261 | 21.6 | 1.6133 | 806.0558 | 649726.0065 | 17410.806 | 1300.4367
2024-10-22 11:40:00 | 290.7011 | 22.0267 | 1.3333 | 812.7133 | 660502.9622 | 17901.3657 | 1083.6178
2024-10-22 11:45:00 | 293.249 | 22.1267 | 1.505 | 819.4842 | 671554.2994 | 18132.453 | 1233.3237
2024-10-22 11:50:00 | 296.137 | 22.0667 | 2 | 825.2492 | 681036.1871 | 18210.4983 | 1650.4983
2024-10-22 11:55:00 | 298.2048 | 21.8267 | 2.4633 | 832.1725 | 692511.0698 | 18163.5518 | 2049.9183
2024-10-22 12:00:00 | 299.8314 | 22.1333 | 1.6433 | 838.0058 | 702253.7767 | 18547.8624 | 1377.1229
2024-10-22 12:05:00 | 300.9845 | 22.2933 | 2.2467 | 843.835 | 712057.5072 | 18811.8949 | 1895.816
2024-10-22 12:10:00 | 303.6271 | 21.86 | 2.325 | 848.3817 | 719751.4523 | 18545.6232 | 1972.4874
2024-10-22 12:15:00 | 302.7822 | 22.0333 | 2.0133 | 852.4717 | 726707.9425 | 18782.7924 | 1716.3096
2024-10-22 12:20:00 | 303.4515 | 21.8467 | 2.3317 | 855.6858 | 732198.2454 | 18693.8832 | 1995.1741
2024-10-22 12:25:00 | 305.3904 | 21.9867 | 2.545 | 859.4342 | 738627.0868 | 18896.0925 | 2187.26
2024-10-22 12:30:00 | 306.4832 | 21.7067 | 2.31 | 861.2808 | 741804.6739 | 18695.536 | 1989.5587
2024-10-22 12:35:00 | 307.4245 | 21.7883 | 2.105 | 863.0242 | 744810.7123 | 18803.8582 | 1816.6659
2024-10-22 12:40:00 | 307.3841 | 21.8117 | 2.1933 | 863.7925 | 746137.4831 | 18840.7541 | 1894.5849
2024-10-22 12:45:00 | 306.7639 | 21.6717 | 2.0583 | 864.185 | 746815.7142 | 18728.3293 | 1778.7808
2024-10-22 12:50:00 | 307.4919 | 21.725 | 2.8533 | 863.6075 | 745817.9141 | 18761.8729 | 2464.1601
2024-10-22 12:55:00 | 306.1425 | 21.4 | 2.3583 | 861.4933 | 742170.7634 | 18435.9573 | 2031.6884
2024-10-22 13:00:00 | 304.1259 | 21.5717 | 2.6133 | 858.3658 | 736791.9038 | 18516.3816 | 2243.196
2024-10-22 13:05:00 | 302.8959 | 21.5567 | 2.435 | 855.1442 | 731271.5458 | 18434.0578 | 2082.276
2024-10-22 13:10:00 | 302.53 | 21.3 | 1.7433 | 851.1383 | 724436.4625 | 18129.2465 | 1483.8178
2024-10-22 13:15:00 | 300.0109 | 21.875 | 1.9083 | 850.5458 | 723428.2146 | 18605.6901 | 1623.125
2024-10-22 13:20:00 | 299.2477 | 21.915 | 2.0817 | 844.5008 | 713181.6575 | 18507.2358 | 1757.9692
2024-10-22 13:25:00 | 295.787 | 22.4317 | 1.8333 | 839.6967 | 705090.492 | 18835.7957 | 1539.4439
2024-10-22 13:30:00 | 294.9293 | 22.18 | 2.25 | 836.2417 | 699300.1251 | 18547.8402 | 1881.5437
2024-10-22 13:35:00 | 293.8565 | 22.5783 | 2.195 | 830.7475 | 690141.4088 | 18756.894 | 1823.4908
2024-10-22 13:40:00 | 291.5968 | 22.5967 | 2.2867 | 824.1325 | 679194.3776 | 18622.6474 | 1884.5163
2024-10-22 13:45:00 | 288.4693 | 22.695 | 1.9233 | 818.6025 | 670110.053 | 18578.1837 | 1574.4455
2024-10-22 13:50:00 | 284.8056 | 22.9867 | 1.7333 | 812.2792 | 659797.4446 | 18671.5904 | 1407.9506
2024-10-22 13:55:00 | 282.0929 | 23.1483 | 1.9433 | 805.2842 | 648482.5891 | 18640.9863 | 1564.9356
2024-10-22 14:00:00 | 277.865 | 22.9367 | 2.2733 | 797.6358 | 636222.9226 | 18295.1072 | 1813.2921
2024-10-22 14:05:00 | 274.5203 | 22.5967 | 2.1717 | 791.46 | 626408.9316 | 17884.3578 | 1718.7873
2024-10-22 14:10:00 | 272.126 | 22.83 | 1.7267 | 784.2117 | 614987.9381 | 17903.5523 | 1354.0721
2024-10-22 14:15:00 | 268.0741 | 23.0567 | 1.935 | 774.8642 | 600414.4768 | 17865.7848 | 1499.3622
2024-10-22 14:20:00 | 265.3206 | 23.33 | 1.42 | 762.8375 | 581921.0514 | 17796.9989 | 1083.2292
2024-10-22 14:25:00 | 260.5314 | 23.3417 | 1.9733 | 751.6925 | 565041.6146 | 17545.7558 | 1483.3399
2024-10-22 14:30:00 | 255.8272 | 23.22 | 2.01 | 741.2408 | 549437.973 | 17211.6122 | 1489.8941
2024-10-22 14:35:00 | 252.1929 | 23.2233 | 1.8817 | 730.7058 | 533931.0149 | 16969.4251 | 1374.9448
2024-10-22 14:40:00 | 248.6008 | 23.185 | 2.285 | 719.7733 | 518073.6514 | 16687.9447 | 1644.6821
2024-10-22 14:45:00 | 242.3332 | 22.8683 | 1.7133 | 706.7958 | 499560.35 | 16163.2427 | 1210.9769
2024-10-22 14:50:00 | 238.2677 | 23.375 | 1.7083 | 695.4233 | 483613.6125 | 16255.5204 | 1188.0149
2024-10-22 14:55:00 | 231.6403 | 22.985 | 1.7733 | 682.5375 | 465857.4389 | 15688.1244 | 1210.3665
2024-10-22 15:00:00 | 226.4051 | 23.2117 | 2.3317 | 670.8792 | 450078.8563 | 15572.2236 | 1564.2666
2024-10-22 15:05:00 | 221.5063 | 22.985 | 1.95 | 657.4725 | 432270.0883 | 15112.0054 | 1282.0714
2024-10-23 11:00:00 | 263.0318 | 23.6933 | 0.62 | 732.1892 | 536100.9758 | 17348.002 | 453.9573
2024-10-23 11:05:00 | 266.7636 | 23.84 | 0.825 | 740.6383 | 548545.1408 | 17656.8179 | 611.0266
2024-10-23 11:10:00 | 269.2766 | 24.3 | 0.85667 | 749.9608 | 562441.2515 | 18224.0482 | 642.4664
2024-10-23 11:15:00 | 271.6603 | 24.22 | 0.99167 | 759.1067 | 576242.9314 | 18385.5635 | 752.7808
2024-10-23 11:20:00 | 275.4223 | 24.4 | 0.75667 | 768.1392 | 590037.7794 | 18742.5957 | 581.2253
2024-10-23 11:25:00 | 277.9104 | 25.1933 | 1.17 | 777.4758 | 604468.6714 | 19587.2078 | 909.6467
2024-10-23 11:30:00 | 279.8142 | 25.7667 | 1.1783 | 785.6392 | 617228.9002 | 20243.3025 | 925.7448
2024-10-23 11:35:00 | 282.7941 | 26.54 | 1.155 | 791.1875 | 625977.6602 | 20998.1162 | 913.8216
2024-10-23 11:40:00 | 285.0285 | 26.3733 | 1.1167 | 796.2692 | 634044.5858 | 21000.2722 | 889.1672
2024-10-23 11:45:00 | 287.6456 | 26.5267 | 1.7717 | 803.4925 | 645600.1976 | 21313.9777 | 1423.5209
2024-10-23 11:50:00 | 288.3707 | 26.3467 | 1.6767 | 807.6117 | 652236.6041 | 21277.8754 | 1354.0956
2024-10-23 11:55:00 | 289.3215 | 26.0133 | 1.5783 | 812.9208 | 660840.2813 | 21146.7806 | 1283.06
2024-10-23 12:00:00 | 291.853 | 26 | 1.805 | 819.5425 | 671649.9093 | 21308.105 | 1479.2742
2024-10-23 12:05:00 | 294.3159 | 26.02 | 1.3017 | 825.29 | 681103.5841 | 21474.0458 | 1074.2525
2024-10-23 12:10:00 | 294.6191 | 25.8867 | 1.68 | 828.6425 | 686648.3928 | 21450.7922 | 1392.1194
2024-10-23 12:15:00 | 295.086 | 25.5133 | 1.8433 | 832.475 | 693014.6256 | 21239.2122 | 1534.5289
2024-10-23 12:20:00 | 297.1146 | 25.3 | 1.4733 | 839.0617 | 704024.4805 | 21228.2602 | 1236.2175
2024-10-23 12:25:00 | 298.0672 | 25.4067 | 1.8417 | 844.425 | 713053.5806 | 21454.0245 | 1555.1494
2024-10-23 12:30:00 | 300.4206 | 25.1533 | 1.5117 | 848.955 | 720724.592 | 21354.0481 | 1283.337
2024-10-23 12:35:00 | 300.5208 | 25.4933 | 1.7033 | 852.7508 | 727183.9838 | 21739.4612 | 1452.5189
2024-10-23 12:40:00 | 302.2555 | 25.3933 | 1.8017 | 855.3967 | 731703.4573 | 21721.3727 | 1541.1397
2024-10-23 12:45:00 | 300.6725 | 25.6 | 1.92 | 855.7233 | 732262.4232 | 21906.5173 | 1642.9888
2024-10-23 12:50:00 | 302.0256 | 25.1133 | 2.3917 | 855.6742 | 732178.2795 | 21488.8306 | 2046.4874
2024-10-23 12:55:00 | 301.5592 | 25.4067 | 1.885 | 854.0617 | 729421.3305 | 21698.8601 | 1609.9062
2024-10-23 13:00:00 | 300.5325 | 25.3 | 2.0617 | 852.2067 | 726256.2027 | 21560.8287 | 1756.9661
2024-10-23 13:05:00 | 299.0437 | 24.8333 | 2.4133 | 849.2075 | 721153.3781 | 21088.6529 | 2049.4208
2024-10-23 13:10:00 | 299.0617 | 24.6867 | 2.0933 | 846.7633 | 717008.1427 | 20903.7642 | 1772.5579
2024-10-23 13:15:00 | 295.2818 | 24.5733 | 2.015 | 843.4917 | 711478.1917 | 20727.4019 | 1699.6357
2024-10-23 13:20:00 | 296.3034 | 24.66 | 2.1283 | 839.2008 | 704258.0387 | 20694.6926 | 1786.0991
2024-10-23 13:25:00 | 292.9866 | 24.6733 | 1.9717 | 833.8725 | 695343.3463 | 20574.4142 | 1644.1186
2024-10-23 13:30:00 | 289.8878 | 24.82 | 2.3033 | 829.1925 | 687560.2021 | 20580.5579 | 1909.9067
2024-10-23 13:35:00 | 288.8185 | 24.92 | 1.7233 | 824.2883 | 679451.2565 | 20541.2653 | 1420.5236
2024-10-23 13:40:00 | 285.6101 | 24.9933 | 1.5733 | 817.5033 | 668311.7 | 20432.1333 | 1286.2052
2024-10-23 13:45:00 | 282.8339 | 25.3667 | 1.04 | 810.4792 | 656876.4796 | 20559.1549 | 842.8983
2024-10-23 13:50:00 | 279.6538 | 25.2267 | 1.8217 | 804.3592 | 646993.669 | 20291.3006 | 1465.2743
2024-10-23 13:55:00 | 276.5657 | 25.3533 | 1.7233 | 797.36 | 635782.9696 | 20215.7339 | 1374.1171
2024-10-23 14:00:00 | 274.5909 | 25.3133 | 2.115 | 790.735 | 625261.8402 | 20016.1386 | 1672.4045
2024-10-23 14:05:00 | 271.3225 | 25.5467 | 1.4933 | 783.58 | 613997.6164 | 20017.8571 | 1170.1461
2024-10-23 14:10:00 | 268.6038 | 26.2467 | 1.4867 | 775.1975 | 600931.164 | 20346.3504 | 1152.4603
2024-10-23 14:15:00 | 263.9129 | 26.34 | 1.8333 | 766.1542 | 586992.2071 | 20180.5007 | 1404.616
2024-10-23 14:20:00 | 260.0111 | 26.2467 | 1.855 | 756.2675 | 571940.5316 | 19849.501 | 1402.8762
2024-10-23 14:25:00 | 257.2296 | 26.3933 | 1.835 | 746.7208 | 557592.0029 | 19708.4519 | 1370.2327
2024-10-23 14:30:00 | 252.6432 | 26.1933 | 1.9083 | 737.8992 | 544495.1802 | 19328.0388 | 1408.1576
2024-10-23 14:35:00 | 249.0556 | 26.4533 | 1.8467 | 727.4608 | 529199.264 | 19243.7639 | 1343.3777
2024-10-23 14:40:00 | 245.3358 | 26.4333 | 1.7833 | 717.1275 | 514271.8513 | 18956.0702 | 1278.8774
2024-10-23 14:45:00 | 239.7557 | 26.48 | 1.9617 | 706.485 | 499121.0552 | 18707.7228 | 1385.8881
2024-10-23 14:50:00 | 235.1951 | 26.6267 | 1.4833 | 695.2025 | 483306.516 | 18510.9252 | 1031.217
2024-10-23 14:55:00 | 229.9629 | 27.1467 | 1.2683 | 682.4383 | 465722.0788 | 18525.926 | 865.5593
2024-10-23 15:00:00 | 224.2101 | 27.2267 | 1.6833 | 668.805 | 447300.128 | 18209.3308 | 1125.8217
2024-10-23 15:05:00 | 219.3073 | 27.2733 | 1.465 | 654.5483 | 428433.5207 | 17851.7149 | 958.9133
2024-10-24 11:00:00 | 264.12 | 20.3867 | 1.7917 | 734.0775 | 538869.776 | 14965.3933 | 1315.2222
2024-10-24 11:05:00 | 268.236 | 20.2467 | 1.5767 | 743.3592 | 552582.8507 | 15050.5453 | 1172.0296
2024-10-24 11:10:00 | 270.5164 | 20.4667 | 2.0483 | 753.825 | 568252.1306 | 15428.285 | 1544.0849
2024-10-24 11:15:00 | 274.4991 | 20.6267 | 1.62 | 763.0833 | 582296.1736 | 15739.8656 | 1236.195
2024-10-24 11:20:00 | 279.3866 | 20.6933 | 2.125 | 771.9658 | 595931.2478 | 15974.5463 | 1640.4274
2024-10-24 11:25:00 | 280.8998 | 20.62 | 2.0433 | 781.0575 | 610050.8183 | 16105.4057 | 1595.9608
2024-10-24 11:30:00 | 283.9716 | 21.06 | 1.87 | 788.0158 | 620968.9536 | 16595.6135 | 1473.5896
2024-10-24 11:35:00 | 286.4598 | 20.54 | 2.4 | 795.6042 | 632985.99 | 16341.7096 | 1909.45
2024-10-24 11:40:00 | 288.3667 | 20.2533 | 2.555 | 802.1767 | 643487.4045 | 16246.7514 | 2049.5614
2024-10-24 11:45:00 | 290.1754 | 20.2333 | 1.79 | 808.2308 | 653237.08 | 16353.2039 | 1446.7332
2024-10-24 11:50:00 | 291.5946 | 20.3333 | 2.2817 | 814.285 | 663060.0612 | 16557.1283 | 1857.9269
2024-10-24 11:55:00 | 292.5038 | 19.9667 | 1.9717 | 821.805 | 675363.458 | 16408.7065 | 1620.3255
2024-10-24 12:00:00 | 294.688 | 20.18 | 2.1317 | 825.3758 | 681245.2663 | 16656.0843 | 1759.4262
2024-10-24 12:05:00 | 295.8589 | 20.0067 | 2.2833 | 833.4608 | 694656.9607 | 16674.7731 | 1903.0689
2024-10-24 12:10:00 | 297.7403 | 20.16 | 2.2317 | 839.8817 | 705401.214 | 16932.0144 | 1874.3359
2024-10-24 12:15:00 | 297.0208 | 20.3267 | 2.0983 | 842.36 | 709570.3696 | 17122.3709 | 1767.5521
2024-10-24 12:20:00 | 298.3629 | 19.8467 | 2.7367 | 844.4992 | 713178.8425 | 16760.4935 | 2311.1127
2024-10-24 12:25:00 | 299.2553 | 19.7067 | 2.4517 | 849.6042 | 721827.24 | 16742.8661 | 2082.9462
2024-10-24 12:30:00 | 300.6988 | 19.9333 | 2.74 | 852.9167 | 727466.8403 | 17001.4722 | 2336.9917
2024-10-24 12:35:00 | 300.8873 | 19.8067 | 2.535 | 855.7308 | 732275.2591 | 16949.1754 | 2169.2777
2024-10-24 12:40:00 | 300.2317 | 20.0533 | 2.3517 | 858.1658 | 736448.5975 | 17209.0855 | 2018.12
2024-10-24 12:45:00 | 301.5279 | 19.8067 | 3.1767 | 856.0733 | 732861.552 | 16955.9592 | 2719.4596
2024-10-24 12:50:00 | 300.0833 | 19.3933 | 2.8583 | 855.1083 | 731210.2617 | 16583.4009 | 2444.1847
2024-10-24 12:55:00 | 300.9797 | 19.62 | 2.37 | 850.3583 | 723109.2951 | 16684.0305 | 2015.3493
2024-10-24 13:00:00 | 300.2863 | 19.9667 | 2.3233 | 853.0467 | 727688.6155 | 17032.4984 | 1981.9118
2024-10-24 13:05:00 | 299.3001 | 19.8 | 2.4683 | 848.6083 | 720136.1034 | 16802.445 | 2094.6482
2024-10-24 13:10:00 | 296.5134 | 19.7667 | 2.55 | 846.8658 | 717181.7397 | 16739.7146 | 2159.5079
2024-10-24 13:15:00 | 293.6099 | 19.7733 | 2.255 | 842.4767 | 709766.9339 | 16658.572 | 1899.7849
2024-10-24 13:20:00 | 293.8651 | 19.6933 | 2.49 | 836.7617 | 700170.0868 | 16478.6264 | 2083.5366
2024-10-24 13:25:00 | 292.4049 | 19.9067 | 2.7533 | 832.5283 | 693103.4258 | 16572.864 | 2292.228
2024-10-24 13:30:00 | 288.5618 | 19.76 | 1.755 | 826.7375 | 683494.8939 | 16336.333 | 1450.9243
2024-10-24 13:35:00 | 285.218 | 20.1733 | 1.9183 | 817.1883 | 667796.7721 | 16485.4126 | 1567.6396
2024-10-24 13:40:00 | 284.9702 | 20.3533 | 1.9883 | 813.3517 | 661540.9337 | 16554.4176 | 1617.2142
2024-10-24 13:45:00 | 279.7142 | 20.22 | 2.66 | 809.9817 | 656070.3003 | 16377.8293 | 2154.5512
2024-10-24 13:50:00 | 279.4542 | 19.68 | 2.055 | 801.5308 | 642451.6768 | 15774.1268 | 1647.1459
2024-10-24 13:55:00 | 273.3209 | 19.5533 | 1.915 | 794.305 | 630920.433 | 15531.3104 | 1521.0941
2024-10-24 14:00:00 | 271.725 | 19.2667 | 2.0267 | 784.4067 | 615293.8187 | 15112.9018 | 1589.7308
2024-10-24 14:05:00 | 270.3719 | 19.8133 | 2.36 | 781.5883 | 610880.3228 | 15485.8702 | 1844.5485
2024-10-24 14:10:00 | 262.8854 | 20.0018 | 2.0217 | 771.3158 | 594928.1148 | 15427.6699 | 1559.3435
2024-10-24 14:15:00 | 262.7816 | 19.93 | 1.835 | 761.3017 | 579580.2277 | 15172.7422 | 1396.9886
2024-10-24 14:20:00 | 259.8132 | 19.6951 | 1.9683 | 764.1216 | 583881.8526 | 15049.4685 | 1504.015
2024-10-24 14:25:00 | 256.7184 | 19.6867 | 2.47 | 743.9642 | 553482.6813 | 14646.1746 | 1837.5915
2024-10-24 14:30:00 | 250.6586 | 19.5267 | 1.975 | 732.1892 | 536100.9758 | 14297.2138 | 1446.0736
2024-10-24 14:35:00 | 248.0095 | 19.52 | 2.425 | 723.0808 | 522845.8915 | 14114.5379 | 1753.471
2024-10-24 14:40:00 | 243.5611 | 19.3733 | 2.13 | 710.9508 | 505451.0874 | 13773.4875 | 1514.3253
2024-10-24 14:45:00 | 236.4688 | 19.6467 | 1.52 | 695.4242 | 483614.7716 | 13662.7668 | 1057.0447
2024-10-24 14:50:00 | 231.5981 | 19.5667 | 2.6383 | 683.0708 | 466585.7634 | 13365.4193 | 1802.1685
2024-10-24 14:55:00 | 226.3011 | 19.3667 | 2.5733 | 674.8275 | 455392.1548 | 13069.1593 | 1736.5561
2024-10-24 15:00:00 | 219.4662 | 19.3267 | 1.9383 | 655.2208 | 429314.3404 | 12663.2346 | 1270.0364

## Modeled (Retained)
timestamp | power | t_amb | w_vel | e_total | e_sq | e_t | e_v | Target Capacity Data after filtering (feeds the Target Capacity regression)
1990-09-20 11:00:00 | 316.59 | 22 | 3 | 815.2885 | 664695.3382 | 17936.347 | 2445.8655
1990-09-20 13:00:00 | 341.48 | 21 | 3 | 873.2817 | 762620.9276 | 18338.9157 | 2619.8451 | Column | Meaning (ASTM E2848: P = E·(a1 + a2·E + a3·T + a4·v))
1990-09-20 14:00:00 | 264.9 | 20 | 3 | 695.7628 | 484085.8739 | 13915.256 | 2087.2884 | timestamp | Record timestamp
1990-09-23 11:00:00 | 340.33 | 20 | 2 | 873.1113 | 762323.3422 | 17462.226 | 1746.2226 | power | Power output — the regression's dependent variable
1990-09-23 12:00:00 | 352.28 | 20 | 3 | 901.2448 | 812242.1895 | 18024.896 | 2703.7344 | t_amb | Ambient air temperature T (°C)
1990-09-23 13:00:00 | 319.27 | 20 | 3 | 820.8982 | 673873.8548 | 16417.964 | 2462.6946 | w_vel | Wind speed v (m/s)
1990-09-24 09:00:00 | 294.24 | 21 | 1 | 769.4357 | 592031.2964 | 16158.1497 | 769.4357 | e_total | Plane-of-array irradiance E (W/m²); for bifacial systems the total effective irradiance including the rear side
1990-09-24 10:00:00 | 349.61 | 21 | 2 | 905.4239 | 819792.4387 | 19013.9019 | 1810.8478 | e_sq | Regressor E² — e_total squared (live formula)
1990-09-24 13:00:00 | 331.99 | 22 | 3 | 860.4885 | 740440.4586 | 18930.747 | 2581.4655 | e_t | Regressor E·T — e_total × t_amb (live formula)
1990-09-24 14:00:00 | 264.62 | 21 | 3 | 705.6192 | 497898.4554 | 14818.0032 | 2116.8576 | e_v | Regressor E·v — e_total × w_vel (live formula)
1990-09-25 09:00:00 | 293 | 22 | 1 | 769.2234 | 591704.6391 | 16922.9148 | 769.2234
1990-09-25 10:00:00 | 341.14 | 22 | 2 | 884.0329 | 781514.1683 | 19448.7238 | 1768.0658
1990-09-25 13:00:00 | 323.08 | 24 | 4 | 841.5243 | 708163.1475 | 20196.5832 | 3366.0972
1990-09-25 14:00:00 | 259.57 | 22 | 3 | 695.0538 | 483099.7849 | 15291.1836 | 2085.1614
1990-09-26 09:00:00 | 291.28 | 23 | 2 | 768.4695 | 590545.3724 | 17674.7985 | 1536.939
1990-09-26 10:00:00 | 342.49 | 23 | 2 | 891.9748 | 795619.0438 | 20515.4204 | 1783.9496
1990-09-26 13:00:00 | 323.9 | 24 | 3 | 844.2282 | 712721.2537 | 20261.4768 | 2532.6846
1990-09-26 14:00:00 | 257.5 | 22 | 3 | 691.1052 | 477626.3975 | 15204.3144 | 2073.3156
1990-09-27 11:00:00 | 316.12 | 20 | 3 | 808.6002 | 653834.2834 | 16172.004 | 2425.8006
1990-09-27 12:00:00 | 344.93 | 20 | 3 | 882.9355 | 779575.0972 | 17658.71 | 2648.8065
1990-09-27 13:00:00 | 298.61 | 21 | 4 | 768.269 | 590237.2564 | 16133.649 | 3073.076
1990-09-28 11:00:00 | 302.58 | 19 | 3 | 770.2891 | 593345.2976 | 14635.4929 | 2310.8673
1990-09-28 13:00:00 | 315.18 | 20 | 4 | 811.0435 | 657791.5589 | 16220.87 | 3244.174
1990-09-28 14:00:00 | 250.59 | 20 | 4 | 669.285 | 447942.4112 | 13385.7 | 2677.14
1990-09-29 09:00:00 | 251.77 | 20 | 2 | 654.6732 | 428596.9988 | 13093.464 | 1309.3464
1990-09-29 10:00:00 | 331.83 | 19 | 2 | 853.0133 | 727631.69 | 16207.2527 | 1706.0266
1990-09-29 12:00:00 | 353.46 | 19 | 3 | 902.7135 | 814891.6631 | 17151.5565 | 2708.1405
1990-09-29 13:00:00 | 315.59 | 20 | 4 | 813.216 | 661320.2627 | 16264.32 | 3252.864
1990-10-01 09:00:00 | 284.42 | 24 | 4 | 754.6184 | 569448.9296 | 18110.8416 | 3018.4736
1990-10-01 10:00:00 | 335.3 | 26 | 4 | 881.4789 | 777005.0511 | 22918.4514 | 3525.9156
1990-10-01 11:00:00 | 349.15 | 26 | 4 | 911.3736 | 830601.8388 | 23695.7136 | 3645.4944
1990-10-01 12:00:00 | 344.73 | 26 | 2 | 898.9323 | 808079.28 | 23372.2398 | 1797.8646
1990-10-01 13:00:00 | 298.96 | 27 | 2 | 784.6267 | 615639.0584 | 21184.9209 | 1569.2534
1990-10-02 09:00:00 | 287.12 | 23 | 2 | 759.2876 | 576517.6595 | 17463.6148 | 1518.5752
1990-10-02 10:00:00 | 333.62 | 24 | 2 | 872.3919 | 761067.6272 | 20937.4056 | 1744.7838
1990-10-02 13:00:00 | 298.2 | 24 | 3 | 775.4756 | 601362.4062 | 18611.4144 | 2326.4268
1990-10-03 10:00:00 | 337.3 | 19 | 2 | 869.5618 | 756137.724 | 16521.6742 | 1739.1236
1990-10-03 11:00:00 | 347.21 | 19 | 3 | 886.9841 | 786740.7937 | 16852.6979 | 2660.9523
1990-10-03 12:00:00 | 340.36 | 20 | 3 | 870.4283 | 757645.4254 | 17408.566 | 2611.2849
1990-10-03 13:00:00 | 314.5 | 20 | 4 | 810.862 | 657497.183 | 16217.24 | 3243.448
1990-10-04 10:00:00 | 340.69 | 17 | 7 | 872.8572 | 761879.6916 | 14838.5724 | 6110.0004
1990-10-04 12:00:00 | 341.49 | 17 | 8 | 865.9019 | 749786.1004 | 14720.3323 | 6927.2152
1990-10-04 13:00:00 | 287.88 | 17 | 8 | 732.9254 | 537179.642 | 12459.7318 | 5863.4032
1990-10-05 09:00:00 | 277.65 | 15 | 1 | 715.7733 | 512331.417 | 10736.5995 | 715.7733
1990-10-05 10:00:00 | 329.1 | 16 | 2 | 839.0519 | 704008.0909 | 13424.8304 | 1678.1038
1990-10-05 12:00:00 | 346.72 | 17 | 4 | 880.2907 | 774911.7165 | 14964.9419 | 3521.1628
1990-10-05 13:00:00 | 298.09 | 16 | 4 | 757.9059 | 574421.3533 | 12126.4944 | 3031.6236
1990-10-06 10:00:00 | 325.65 | 17 | 2 | 832.8059 | 693565.6671 | 14157.7003 | 1665.6118
1990-10-06 11:00:00 | 349.6 | 18 | 3 | 890.9043 | 793710.4718 | 16036.2774 | 2672.7129
1990-10-06 12:00:00 | 330.03 | 18 | 3 | 838.5194 | 703114.7842 | 15093.3492 | 2515.5582
1990-10-06 13:00:00 | 290.83 | 18 | 4 | 743.6343 | 552991.9721 | 13385.4174 | 2974.5372
1990-10-07 10:00:00 | 324 | 17 | 2 | 828.4401 | 686312.9993 | 14083.4817 | 1656.8802
1990-10-07 11:00:00 | 346.59 | 17 | 3 | 881.0614 | 776269.1906 | 14978.0438 | 2643.1842
1990-10-07 12:00:00 | 346.34 | 18 | 3 | 882.4142 | 778654.8204 | 15883.4556 | 2647.2426
1990-10-07 13:00:00 | 310.29 | 18 | 2 | 797.5463 | 636080.1006 | 14355.8334 | 1595.0926
1990-10-08 09:00:00 | 266.19 | 17 | 2 | 689.6453 | 475610.6398 | 11723.9701 | 1379.2906
1990-10-08 10:00:00 | 326.75 | 18 | 2 | 838.7534 | 703507.266 | 15097.5612 | 1677.5068
1990-10-08 12:00:00 | 328.71 | 18 | 3 | 840.2867 | 706081.7382 | 15125.1606 | 2520.8601
1990-10-08 13:00:00 | 302.3 | 18 | 4 | 775.779 | 601833.0568 | 13964.022 | 3103.116
1990-10-09 11:00:00 | 317.81 | 17 | 3 | 811.0718 | 657837.4648 | 13788.2206 | 2433.2154
1990-10-09 12:00:00 | 303.64 | 17 | 3 | 773.9349 | 598975.2294 | 13156.8933 | 2321.8047
1990-10-10 11:00:00 | 324.33 | 16 | 2 | 826.2366 | 682666.9192 | 13219.7856 | 1652.4732
1990-10-10 12:00:00 | 327.4 | 16 | 3 | 832.1602 | 692490.5985 | 13314.5632 | 2496.4806
1990-10-10 13:00:00 | 303.27 | 17 | 3 | 777.8138 | 604994.3075 | 13222.8346 | 2333.4414
1990-10-15 10:00:00 | 328.73 | 21 | 2 | 854.9313 | 730907.5277 | 17953.5573 | 1709.8626
1990-10-15 11:00:00 | 350.36 | 21 | 2 | 908.4863 | 825347.3573 | 19078.2123 | 1816.9726
1990-10-15 12:00:00 | 341.46 | 21 | 3 | 884.6664 | 782634.6393 | 18577.9944 | 2653.9992
1990-10-15 13:00:00 | 300.39 | 22 | 2 | 787.0051 | 619377.0274 | 17314.1122 | 1574.0102
1990-10-16 10:00:00 | 323.44 | 26 | 1 | 853.2491 | 728034.0267 | 22184.4766 | 853.2491
1990-10-16 11:00:00 | 338.99 | 26 | 1 | 891.1571 | 794160.9769 | 23170.0846 | 891.1571
1990-10-16 12:00:00 | 331.95 | 26 | 2 | 872.1501 | 760645.7969 | 22675.9026 | 1744.3002
1990-10-16 13:00:00 | 295.46 | 26 | 2 | 783.3028 | 613563.2765 | 20365.8728 | 1566.6056
1990-10-17 10:00:00 | 304.86 | 24 | 2 | 796.1558 | 633864.0579 | 19107.7392 | 1592.3116
1990-10-17 11:00:00 | 316.28 | 24 | 2 | 822.2102 | 676029.613 | 19733.0448 | 1644.4204
1990-10-17 12:00:00 | 304.47 | 24 | 2 | 790.8391 | 625426.4821 | 18980.1384 | 1581.6782
1990-10-17 13:00:00 | 278.95 | 24 | 2 | 732.0231 | 535857.8189 | 17568.5544 | 1464.0462
1990-10-19 11:00:00 | 326.18 | 18 | 3 | 835.2048 | 697567.0579 | 15033.6864 | 2505.6144
1990-10-19 12:00:00 | 315.77 | 19 | 4 | 809.6807 | 655582.836 | 15383.9333 | 3238.7228
1990-10-19 13:00:00 | 288.45 | 19 | 4 | 749.3911 | 561587.0208 | 14238.4309 | 2997.5644
1990-10-20 10:00:00 | 316.89 | 19 | 2 | 819.1944 | 671079.465 | 15564.6936 | 1638.3888
1990-10-20 11:00:00 | 320.4 | 19 | 3 | 821.874 | 675476.8719 | 15615.606 | 2465.622
1990-10-20 12:00:00 | 309.37 | 20 | 3 | 794.3853 | 631048.0049 | 15887.706 | 2383.1559
1990-10-20 13:00:00 | 273.53 | 20 | 3 | 711.2202 | 505834.1729 | 14224.404 | 2133.6606
1990-10-21 10:00:00 | 306.85 | 21 | 1 | 795.886 | 633434.525 | 16713.606 | 795.886
1990-10-21 11:00:00 | 340.84 | 21 | 2 | 884.5035 | 782346.4415 | 18574.5735 | 1769.007
1990-10-21 12:00:00 | 332.1 | 21 | 3 | 860.2253 | 739987.5668 | 18064.7313 | 2580.6759
1990-10-21 13:00:00 | 283.82 | 21 | 2 | 742.6288 | 551497.5346 | 15595.2048 | 1485.2576
1990-10-22 10:00:00 | 304.6 | 21 | 1 | 790.6707 | 625160.1558 | 16604.0847 | 790.6707
1990-10-22 11:00:00 | 323.01 | 21 | 2 | 834.6156 | 696583.1998 | 17526.9276 | 1669.2312
1990-10-22 12:00:00 | 322.25 | 21 | 3 | 832.8315 | 693608.3074 | 17489.4615 | 2498.4945
1990-10-23 10:00:00 | 303.1 | 22 | 2 | 789.2141 | 622858.8956 | 17362.7102 | 1578.4282
1990-10-23 11:00:00 | 330.71 | 22 | 2 | 858.9811 | 737848.5302 | 18897.5842 | 1717.9622
1990-10-23 12:00:00 | 318.17 | 22 | 3 | 824.6704 | 680081.2686 | 18142.7488 | 2474.0112
1990-10-24 10:00:00 | 291.15 | 21 | 2 | 755.6089 | 570944.8098 | 15867.7869 | 1511.2178
1990-10-24 11:00:00 | 323.6 | 21 | 2 | 836.9541 | 700492.1655 | 17576.0361 | 1673.9082
1990-10-24 12:00:00 | 324.29 | 21 | 2 | 840.1721 | 705889.1576 | 17643.6141 | 1680.3442
1990-10-25 10:00:00 | 296.44 | 22 | 1 | 772.5295 | 596801.8284 | 16995.649 | 772.5295
1990-10-25 11:00:00 | 304.19 | 23 | 2 | 788.3418 | 621482.7936 | 18131.8614 | 1576.6836
1990-10-25 12:00:00 | 292.13 | 24 | 2 | 758.8961 | 575923.2906 | 18213.5064 | 1517.7922
1990-10-26 10:00:00 | 301.27 | 24 | 1 | 790.777 | 625328.2637 | 18978.648 | 790.777
1990-10-26 11:00:00 | 318.75 | 24 | 1 | 831.162 | 690830.2702 | 19947.888 | 831.162
1990-10-26 12:00:00 | 306.56 | 24 | 2 | 798.5628 | 637702.5455 | 19165.5072 | 1597.1256
1990-10-27 10:00:00 | 303 | 19 | 3 | 784.7834 | 615884.9849 | 14910.8846 | 2354.3502
1990-10-27 11:00:00 | 321.73 | 20 | 4 | 831.598 | 691555.2336 | 16631.96 | 3326.392
1990-10-27 12:00:00 | 276 | 20 | 4 | 710.2994 | 504525.2376 | 14205.988 | 2841.1976
1990-10-28 10:00:00 | 296.56 | 15 | 2 | 758.1402 | 574776.5629 | 11372.103 | 1516.2804
1990-10-28 11:00:00 | 315.47 | 16 | 2 | 804.0433 | 646485.6283 | 12864.6928 | 1608.0866
1990-10-28 12:00:00 | 311.75 | 16 | 3 | 794.2445 | 630824.3258 | 12707.912 | 2382.7335
1990-10-29 10:00:00 | 306.47 | 16 | 1 | 788.81 | 622221.2161 | 12620.96 | 788.81
1990-10-29 11:00:00 | 326.77 | 17 | 2 | 837.1724 | 700857.6273 | 14231.9308 | 1674.3448
1990-10-29 12:00:00 | 312.82 | 17 | 2 | 800.3077 | 640492.4147 | 13605.2309 | 1600.6154
1990-10-30 11:00:00 | 326.72 | 18 | 2 | 840.5148 | 706465.129 | 15129.2664 | 1681.0296
1990-10-30 12:00:00 | 315.9 | 17 | 2 | 809.8739 | 655895.7339 | 13767.8563 | 1619.7478
1990-10-31 11:00:00 | 316.94 | 20 | 2 | 819.405 | 671424.554 | 16388.1 | 1638.81
1990-10-31 12:00:00 | 308.43 | 20 | 2 | 798.1377 | 637023.7882 | 15962.754 | 1596.2754
1990-11-01 11:00:00 | 311.18 | 17 | 3 | 797.502 | 636009.44 | 13557.534 | 2392.506
1990-11-01 12:00:00 | 298.88 | 17 | 3 | 765.3205 | 585715.4677 | 13010.4485 | 2295.9615
1990-11-02 11:00:00 | 322.7 | 17 | 3 | 829.5589 | 688167.9686 | 14102.5013 | 2488.6767
1990-11-03 11:00:00 | 309.49 | 18 | 2 | 796.8112 | 634908.0884 | 14342.6016 | 1593.6224
1990-11-03 12:00:00 | 303.88 | 18 | 3 | 783.5135 | 613893.4047 | 14103.243 | 2350.5405
1990-11-04 11:00:00 | 307.42 | 19 | 2 | 794.8031 | 631711.9678 | 15101.2589 | 1589.6062
1990-11-04 12:00:00 | 290.11 | 19 | 3 | 749.5221 | 561783.3784 | 14240.9199 | 2248.5663
1990-11-05 11:00:00 | 311.3 | 18 | 2 | 804.0228 | 646452.6629 | 14472.4104 | 1608.0456
1990-11-08 11:00:00 | 261.55 | 14 | 4 | 665.581 | 442998.0676 | 9318.134 | 2662.324
1990-11-08 12:00:00 | 261.12 | 14 | 5 | 665.5766 | 442992.2105 | 9318.0724 | 3327.883

## Calculation
Regression coefficients (Excel LINEST, intercept-free)
Coefficient | Tested (measured), a | Target (modeled), b
1 (E) | 0.29492 | 0.38551
2 (E²) | 5.6969e-05 | 3.1026e-05
3 (E·T) | 0.00044872 | -0.0012421
4 (E·v) | 0.00099158 | 0.0004642
Capacities and Tested Capacity Ratio per reporting condition
Band | E_RC (W/m²) | T_RC (°C) | v_RC (m/s) | Tested Capacity | Target Capacity | Ratio (%)
Low
Mid | 813 | 19.8 | 2.7 | 286.8283 | 314.9489 | 91.1
High
Verdicts (a tier passes when every band it thresholds passes)
Overall verdict (Mid ratio >= 100% - tolerance) | FAIL
Worst-performing ratio (%) | 91.1
Worst-performing band | Mid
All results are live formulas — edit the yellow cells on the Inputs sheet and this sheet recalculates.

## Cross-Check
Quantity | Excel (this workbook) | HelioTest | Δ (Excel − HelioTest)
a1 (Tested regression) | 0.29492 | 0.29492 | 1.1102e-16
a2 (Tested regression) | 5.6969e-05 | 5.6969e-05 | 2.4395e-19
a3 (Tested regression) | 0.00044872 | 0.00044872 | -2.7105e-18
a4 (Tested regression) | 0.00099158 | 0.00099158 | 4.8789e-17
b1 (Target regression) | 0.38551 | 0.38551 | 4.4409e-16
b2 (Target regression) | 3.1026e-05 | 3.1026e-05 | -7.1151e-19
b3 (Target regression) | -0.0012421 | -0.0012421 | -4.3368e-19
b4 (Target regression) | 0.0004642 | 0.0004642 | -2.7268e-17
Capacity ratio — Low (%)
Capacity ratio — Mid (%) | 91.1
Capacity ratio — High (%)
Overall capacity ratio (%) — HelioTest vs Excel Mid | 91.1 | 91.066 | 0.034019
Verdict (Excel: overall ¦ HelioTest: run status) | FAIL | failed
On an unmodified workbook every Δ reads zero and every verdict reads match — Excel independently confirms HelioTest's results.